## Hazard Curves
*Terminologies: PGA (Peak Ground Accerlation), AFE (Annual Frequency of Exceedance)
| Hazard Curve-1 | Hazard Curve-2 | Hazard Curve-3 | Hazard Curve-4 | Hazard Curve-5 | Hazard Curve-6
| Piedomont Mb_max=5.8 | Piedomont Mb_max=6.3 | Northeast Tectonic | Crustal Block Mb,max=5.5 | Crustal Block Mb,max=6.8 | Decollement
Weighting Factors | P=0.15 | P=0.15 | P=0.30 | P=0.15 | P=0.15 | P=0.10
PGA (g) | AFE1 (/yr) | AFE2 (/yr) | AFE3 (/yr) | AFE4 (/yr) | AFE5 (/yr) | AFE6 (/yr)
0.05 | 0.00549 | 0.00281 | 0.00681 | 0.000576 | 0.000972 | 0.00602
0.06 | 0.00375 | 0.00211 | 0.0051 | 0.000383 | 0.000628 | 0.00391
0.07 | 0.00269 | 0.00165 | 0.00394 | 0.000268 | 0.000432 | 0.00271
0.08 | 0.00201 | 0.00133 | 0.00311 | 0.000195 | 0.00031 | 0.00198
0.09 | 0.00155 | 0.0011 | 0.00249 | 0.000146 | 0.000231 | 0.0015
0.1 | 0.00122 | 0.000922 | 0.00201 | 0.000112 | 0.000176 | 0.00117
0.11 | 0.000974 | 0.000785 | 0.00164 | 8.74e-05 | 0.000137 | 0.00093
0.12 | 0.000792 | 0.000677 | 0.00134 | 6.91e-05 | 0.000109 | 0.000757
0.13 | 0.000652 | 0.000589 | 0.00109 | 5.52e-05 | 8.76e-05 | 0.000626
0.14 | 0.000542 | 0.000517 | 0.00089 | 4.45e-05 | 7.13e-05 | 0.000525
0.15 | 0.000454 | 0.000457 | 0.000721 | 3.62e-05 | 5.87e-05 | 0.000446
0.16 | 0.000384 | 0.000407 | 0.000579 | 2.95e-05 | 4.88e-05 | 0.000382
0.17 | 0.000326 | 0.000364 | 0.000459 | 2.42e-05 | 4.08e-05 | 0.000331
0.18 | 0.000279 | 0.000327 | 0.000357 | 1.99e-05 | 3.44e-05 | 0.000289
0.19 | 0.00024 | 0.000295 | 0.00027 | 1.64e-05 | 2.91e-05 | 0.000254
0.2 | 0.000207 | 0.000267 | 0.000196 | 1.36e-05 | 2.48e-05 | 0.000225
0.21 | 0.000179 | 0.000243 | 0.000134 | 1.12e-05 | 2.12e-05 | 0.000201
0.22 | 0.000155 | 0.000221 | 8.09e-05 | 9.25e-06 | 1.82e-05 | 0.00018
0.23 | 0.000135 | 0.000202 | 3.8e-05 | 7.62e-06 | 1.57e-05 | 0.000162
0.24 | 0.000117 | 0.000185 | 5.95e-06 | 6.26e-06 | 1.36e-05 | 0.000146
0.25 | 0.000102 | 0.00017 | 0 | 5.12e-06 | 1.17e-05 | 0.000133
0.26 | 8.94e-05 | 0.000156 | 0 | 4.17e-06 | 1.02e-05 | 0.000121
0.27 | 7.82e-05 | 0.000144 | 0 | 3.38e-06 | 8.86e-06 | 0.000111
0.28 | 6.83e-05 | 0.000133 | 0 | 2.71e-06 | 7.72e-06 | 0.000101
0.29 | 5.98e-05 | 0.000123 | 0 | 2.16e-06 | 6.73e-06 | 9.33e-05
0.3 | 5.23e-05 | 0.000113 | 0 | 1.69e-06 | 5.87e-06 | 8.61e-05
0.31 | 4.57e-05 | 0.000105 | 0 | 1.31e-06 | 5.13e-06 | 7.97e-05
0.32 | 3.99e-05 | 9.73e-05 | 0 | 9.92e-07 | 4.48e-06 | 7.39e-05
0.33 | 3.48e-05 | 9.02e-05 | 0 | 7.33e-07 | 3.91e-06 | 6.87e-05
0.34 | 3.03e-05 | 8.38e-05 | 0 | 5.25e-07 | 3.42e-06 | 6.4e-05
0.35 | 2.63e-05 | 7.78e-05 | 0 | 3.59e-07 | 2.98e-06 | 5.97e-05
0.36 | 2.28e-05 | 7.23e-05 | 0 | 2.3e-07 | 2.6e-06 | 5.59e-05
0.37 | 1.97e-05 | 6.72e-05 | 0 | 1.34e-07 | 2.27e-06 | 5.24e-05
0.38 | 1.7e-05 | 6.25e-05 | 0 | 6.65e-08 | 1.97e-06 | 4.92e-05
0.39 | 1.45e-05 | 5.81e-05 | 0 | 2.35e-08 | 1.72e-06 | 4.62e-05
0.4 | 1.24e-05 | 5.4e-05 | 0 | 2.66e-09 | 1.49e-06 | 4.35e-05
0.41 | 1.05e-05 | 5.03e-05 | 0 | 0 | 1.29e-06 | 4.11e-05
0.42 | 8.88e-06 | 4.67e-05 | 0 | 0 | 1.11e-06 | 3.88e-05
0.43 | 7.43e-06 | 4.35e-05 | 0 | 0 | 9.58e-07 | 3.67e-05
0.44 | 6.16e-06 | 4.04e-05 | 0 | 0 | 8.22e-07 | 3.47e-05
0.45 | 5.05e-06 | 3.76e-05 | 0 | 0 | 7.03e-07 | 3.29e-05
0.46 | 4.09e-06 | 3.49e-05 | 0 | 0 | 5.98e-07 | 3.12e-05
0.47 | 3.26e-06 | 3.24e-05 | 0 | 0 | 5.06e-07 | 2.97e-05
0.48 | 2.55e-06 | 3.01e-05 | 0 | 0 | 4.26e-07 | 2.82e-05
0.49 | 1.94e-06 | 2.79e-05 | 0 | 0 | 3.56e-07 | 2.69e-05
0.5 | 1.43e-06 | 2.59e-05 | 0 | 0 | 2.95e-07 | 2.56e-05
0.51 | 1.02e-06 | 2.39e-05 | 0 | 0 | 2.42e-07 | 2.45e-05
0.52 | 6.79e-07 | 2.21e-05 | 0 | 0 | 1.97e-07 | 2.34e-05
0.53 | 4.16e-07 | 2.04e-05 | 0 | 0 | 1.58e-07 | 2.23e-05
0.54 | 2.21e-07 | 1.89e-05 | 0 | 0 | 1.25e-07 | 2.14e-05
0.55 | 8.85e-08 | 1.74e-05 | 0 | 0 | 9.7e-08 | 2.05e-05
0.56 | 1.59e-08 | 1.6e-05 | 0 | 0 | 7.37e-08 | 1.96e-05
0.57 | 0 | 1.47e-05 | 0 | 0 | 5.44e-08 | 1.88e-05
0.58 | 0 | 1.34e-05 | 0 | 0 | 3.88e-08 | 1.8e-05
0.59 | 0 | 1.23e-05 | 0 | 0 | 2.64e-08 | 1.73e-05
0.6 | 0 | 1.12e-05 | 0 | 0 | 1.68e-08 | 1.66e-05
0.61 | 0 | 1.02e-05 | 0 | 0 | 9.71e-09 | 1.6e-05
0.62 | 0 | 9.2e-06 | 0 | 0 | 4.8e-09 | 1.54e-05
0.63 | 0 | 8.3e-06 | 0 | 0 | 1.76e-09 | 1.48e-05
0.64 | 0 | 7.46e-06 | 0 | 0 | 2.88e-10 | 1.43e-05
0.65 | 0 | 6.67e-06 | 0 | 0 | 0 | 1.38e-05
0.66 | 0 | 5.94e-06 | 0 | 0 | 0 | 1.33e-05
0.67 | 0 | 5.25e-06 | 0 | 0 | 0 | 1.28e-05
0.68 | 0 | 4.61e-06 | 0 | 0 | 0 | 1.24e-05
0.69 | 0 | 4.01e-06 | 0 | 0 | 0 | 1.19e-05
0.7 | 0 | 3.46e-06 | 0 | 0 | 0 | 1.15e-05
0.71 | 0 | 2.94e-06 | 0 | 0 | 0 | 1.12e-05
0.72 | 0 | 2.47e-06 | 0 | 0 | 0 | 1.08e-05
0.73 | 0 | 2.04e-06 | 0 | 0 | 0 | 1.04e-05
0.74 | 0 | 1.64e-06 | 0 | 0 | 0 | 1.01e-05
0.75 | 0 | 1.28e-06 | 0 | 0 | 0 | 9.8e-06
0.76 | 0 | 9.64e-07 | 0 | 0 | 0 | 9.5e-06
0.77 | 0 | 6.82e-07 | 0 | 0 | 0 | 9.21e-06
0.78 | 0 | 4.39e-07 | 0 | 0 | 0 | 8.93e-06
0.79 | 0 | 2.38e-07 | 0 | 0 | 0 | 8.66e-06
0.8 | 0 | 8.45e-08 | 0 | 0 | 0 | 8.41e-06
0.81 | 0 | 0 | 0 | 0 | 0 | 8.16e-06
0.82 | 0 | 0 | 0 | 0 | 0 | 7.93e-06
0.83 | 0 | 0 | 0 | 0 | 0 | 7.71e-06
0.84 | 0 | 0 | 0 | 0 | 0 | 7.49e-06
0.85 | 0 | 0 | 0 | 0 | 0 | 7.28e-06
0.86 | 0 | 0 | 0 | 0 | 0 | 7.08e-06
0.87 | 0 | 0 | 0 | 0 | 0 | 6.89e-06
0.88 | 0 | 0 | 0 | 0 | 0 | 6.71e-06
0.89 | 0 | 0 | 0 | 0 | 0 | 6.53e-06
0.9 | 0 | 0 | 0 | 0 | 0 | 6.36e-06
0.91 | 0 | 0 | 0 | 0 | 0 | 6.19e-06
0.92 | 0 | 0 | 0 | 0 | 0 | 6.04e-06
0.93 | 0 | 0 | 0 | 0 | 0 | 5.88e-06
0.94 | 0 | 0 | 0 | 0 | 0 | 5.74e-06
0.95 | 0 | 0 | 0 | 0 | 0 | 5.59e-06
0.96 | 0 | 0 | 0 | 0 | 0 | 5.46e-06
0.97 | 0 | 0 | 0 | 0 | 0 | 5.32e-06
0.98 | 0 | 0 | 0 | 0 | 0 | 5.2e-06
0.99 | 0 | 0 | 0 | 0 | 0 | 5.07e-06
1 | 0 | 0 | 0 | 0 | 0 | 4.95e-06
1.01 | 0 | 0 | 0 | 0 | 0 | 4.8328e-06
1.02 | 0 | 0 | 0 | 0 | 0 | 4.7185e-06
1.03 | 0 | 0 | 0 | 0 | 0 | 4.6068e-06
1.04 | 0 | 0 | 0 | 0 | 0 | 4.4977e-06
1.05 | 0 | 0 | 0 | 0 | 0 | 4.3913e-06
1.06 | 0 | 0 | 0 | 0 | 0 | 4.2873e-06
1.07 | 0 | 0 | 0 | 0 | 0 | 4.1859e-06
1.08 | 0 | 0 | 0 | 0 | 0 | 4.0868e-06
1.09 | 0 | 0 | 0 | 0 | 0 | 3.9901e-06
1.1 | 0 | 0 | 0 | 0 | 0 | 3.8956e-06
1.11 | 0 | 0 | 0 | 0 | 0 | 3.8034e-06
1.12 | 0 | 0 | 0 | 0 | 0 | 3.7134e-06
1.13 | 0 | 0 | 0 | 0 | 0 | 3.6255e-06
1.14 | 0 | 0 | 0 | 0 | 0 | 3.5397e-06
1.15 | 0 | 0 | 0 | 0 | 0 | 3.4559e-06
1.16 | 0 | 0 | 0 | 0 | 0 | 3.3741e-06
1.17 | 0 | 0 | 0 | 0 | 0 | 3.2943e-06
1.18 | 0 | 0 | 0 | 0 | 0 | 3.2163e-06
1.19 | 0 | 0 | 0 | 0 | 0 | 3.1402e-06
1.2 | 0 | 0 | 0 | 0 | 0 | 3.0658e-06
1.21 | 0 | 0 | 0 | 0 | 0 | 2.9933e-06
1.22 | 0 | 0 | 0 | 0 | 0 | 2.9224e-06
1.23 | 0 | 0 | 0 | 0 | 0 | 2.8533e-06
1.24 | 0 | 0 | 0 | 0 | 0 | 2.7857e-06
1.25 | 0 | 0 | 0 | 0 | 0 | 2.7198e-06
1.26 | 0 | 0 | 0 | 0 | 0 | 2.6554e-06
1.27 | 0 | 0 | 0 | 0 | 0 | 2.5926e-06
1.28 | 0 | 0 | 0 | 0 | 0 | 2.5312e-06
1.29 | 0 | 0 | 0 | 0 | 0 | 2.4713e-06
1.3 | 0 | 0 | 0 | 0 | 0 | 2.4128e-06
1.31 | 0 | 0 | 0 | 0 | 0 | 2.3557e-06
1.32 | 0 | 0 | 0 | 0 | 0 | 2.2999e-06
1.33 | 0 | 0 | 0 | 0 | 0 | 2.2455e-06
1.34 | 0 | 0 | 0 | 0 | 0 | 2.1924e-06
1.35 | 0 | 0 | 0 | 0 | 0 | 2.1405e-06
1.36 | 0 | 0 | 0 | 0 | 0 | 2.0898e-06
1.37 | 0 | 0 | 0 | 0 | 0 | 2.0403e-06
1.38 | 0 | 0 | 0 | 0 | 0 | 1.9921e-06
1.39 | 0 | 0 | 0 | 0 | 0 | 1.9449e-06
1.4 | 0 | 0 | 0 | 0 | 0 | 1.8989e-06
1.41 | 0 | 0 | 0 | 0 | 0 | 1.8539e-06
1.42 | 0 | 0 | 0 | 0 | 0 | 1.81e-06
1.43 | 0 | 0 | 0 | 0 | 0 | 1.7672e-06
1.44 | 0 | 0 | 0 | 0 | 0 | 1.7254e-06
1.45 | 0 | 0 | 0 | 0 | 0 | 1.6845e-06
1.46 | 0 | 0 | 0 | 0 | 0 | 1.6447e-06
1.47 | 0 | 0 | 0 | 0 | 0 | 1.6057e-06
1.48 | 0 | 0 | 0 | 0 | 0 | 1.5677e-06
1.49 | 0 | 0 | 0 | 0 | 0 | 1.5306e-06
1.5 | 0 | 0 | 0 | 0 | 0 | 1.4944e-06
1.51 | 0 | 0 | 0 | 0 | 0 | 1.459e-06
1.52 | 0 | 0 | 0 | 0 | 0 | 1.4245e-06
1.53 | 0 | 0 | 0 | 0 | 0 | 1.3908e-06
1.54 | 0 | 0 | 0 | 0 | 0 | 1.3579e-06
1.55 | 0 | 0 | 0 | 0 | 0 | 1.3257e-06
1.56 | 0 | 0 | 0 | 0 | 0 | 1.2943e-06
1.57 | 0 | 0 | 0 | 0 | 0 | 1.2637e-06
1.58 | 0 | 0 | 0 | 0 | 0 | 1.2338e-06
1.59 | 0 | 0 | 0 | 0 | 0 | 1.2046e-06
1.6 | 0 | 0 | 0 | 0 | 0 | 1.1761e-06
1.61 | 0 | 0 | 0 | 0 | 0 | 1.1483e-06
1.62 | 0 | 0 | 0 | 0 | 0 | 1.1211e-06
1.63 | 0 | 0 | 0 | 0 | 0 | 1.0945e-06
1.64 | 0 | 0 | 0 | 0 | 0 | 1.0686e-06
1.65 | 0 | 0 | 0 | 0 | 0 | 1.0433e-06
1.66 | 0 | 0 | 0 | 0 | 0 | 1.0186e-06
1.67 | 0 | 0 | 0 | 0 | 0 | 9.9454e-07
1.68 | 0 | 0 | 0 | 0 | 0 | 9.71e-07
1.69 | 0 | 0 | 0 | 0 | 0 | 9.4801e-07
1.7 | 0 | 0 | 0 | 0 | 0 | 9.2558e-07
1.71 | 0 | 0 | 0 | 0 | 0 | 9.0367e-07
1.72 | 0 | 0 | 0 | 0 | 0 | 8.8228e-07
1.73 | 0 | 0 | 0 | 0 | 0 | 8.614e-07
1.74 | 0 | 0 | 0 | 0 | 0 | 8.4101e-07
1.75 | 0 | 0 | 0 | 0 | 0 | 8.211e-07
1.76 | 0 | 0 | 0 | 0 | 0 | 8.0167e-07
1.77 | 0 | 0 | 0 | 0 | 0 | 7.827e-07
1.78 | 0 | 0 | 0 | 0 | 0 | 7.6417e-07
1.79 | 0 | 0 | 0 | 0 | 0 | 7.4608e-07
1.8 | 0 | 0 | 0 | 0 | 0 | 7.2842e-07
1.81 | 0 | 0 | 0 | 0 | 0 | 7.1118e-07
1.82 | 0 | 0 | 0 | 0 | 0 | 6.9435e-07
1.83 | 0 | 0 | 0 | 0 | 0 | 6.7792e-07
1.84 | 0 | 0 | 0 | 0 | 0 | 6.6187e-07
1.85 | 0 | 0 | 0 | 0 | 0 | 6.4621e-07
1.86 | 0 | 0 | 0 | 0 | 0 | 6.3091e-07
1.87 | 0 | 0 | 0 | 0 | 0 | 6.1598e-07
1.88 | 0 | 0 | 0 | 0 | 0 | 6.014e-07
1.89 | 0 | 0 | 0 | 0 | 0 | 5.8716e-07
1.9 | 0 | 0 | 0 | 0 | 0 | 5.7327e-07
1.91 | 0 | 0 | 0 | 0 | 0 | 5.597e-07
1.92 | 0 | 0 | 0 | 0 | 0 | 5.4645e-07
1.93 | 0 | 0 | 0 | 0 | 0 | 5.3352e-07
1.94 | 0 | 0 | 0 | 0 | 0 | 5.2089e-07
1.95 | 0 | 0 | 0 | 0 | 0 | 5.0856e-07
1.96 | 0 | 0 | 0 | 0 | 0 | 4.9652e-07
1.97 | 0 | 0 | 0 | 0 | 0 | 4.8477e-07
1.98 | 0 | 0 | 0 | 0 | 0 | 4.733e-07
1.99 | 0 | 0 | 0 | 0 | 0 | 4.621e-07
2 | 0 | 0 | 0 | 0 | 0 | 4.5116e-07

## Fragility Parameters
Structures, Systems and Components (SSCs) | Log-normal Fragility Parameters |  |  | random_failure (/yr)
| Median | Log-normal Stadnard Deviations
| Am (g) | βr | βu
C1: S1 Offsite power | 0.2 | 0.2 | 0.25 | 0
C2: S2 CST | 0.24 | 0.23 | 0.31 | 0
C3: S3 Reactor internals | 0.67 | 0.28 | 0.32 | 0
C4: S4 Reactor enclosure structure | 1.05 | 0.31 | 0.25 | 0
C5: S6 Reactor pressure vessel | 1.25 | 0.28 | 0.22 | 0
C6: S10 SLC tank | 1.33 | 0.27 | 0.19 | 0
C7: S11 440-V bus/SG breakers | 1.46 | 0.38 | 0.44 | 0
C8: S12 440-V bus transformer breaker | 1.49 | 0.36 | 0.43 | 0
C9: S13 125/250-V DC bus | 1.49 | 0.36 | 0.43 | 0
C10: S14 4-kV bus/SG | 1.49 | 0.36 | 0.43 | 0
C11: S15 Diesel generator circuit | 1.56 | 0.32 | 0.41 | 0
C12: S16 Diesel generator heat and vent | 1.55 | 0.28 | 0.43 | 0
C13: S17 RHR heat exchangers | 1.09 | 0.32 | 0.34 | 0
RF1: DGR Diesel generator common mode | 0 | 0 | 0 | 0.00125
RF2: WR Containment heat removal | 0 | 0 | 0 | 0.00026
RF3: CR Scram system mechanical failure | 0 | 0 | 0 | 1e-05
RF4: SLCR Standby liquid control | 0 | 0 | 0 | 0.01

## System Logic Expressions
Symbols: "¦" = OR logic, "&" = AND logic, "~" = Negate logic
Name | System Descriptions | System Equations (Logic Tree) | System Equations (UMB)
TEUX | Loss of high-pressure coolant injection followed by failure to depressurize the reactor | C(:,1) & ( C(:,7) ¦ C(:,8) ¦ C(:,9) ¦ C(:,10) ¦ C(:,11) ¦ C(:,12) ¦ RF(:,1) ) | C(:,1).*( 1 - (1 -C(:,7)).*(1 -C(:,8)).*(1 -C(:,9)).*(1 -C(:,10)).*(1 -C(:,11)).*(1 -C(:,12)).*(1 -RF(:,1)) )
TRpv | Failure of the reactor vessel upper lateral support bracket | C(:,5) | C(:,5)
TRb | Failure of shear walls in the reactor control building | C(:,4) | C(:,4)
TECC | Failure of the standby liquid control system | C(:,1) & (C(:,3)¦RF(:,3)) & (( C(:,7) ¦ C(:,8) ¦ C(:,9) ¦ C(:,10) ¦ C(:,11) ¦ C(:,12) ¦ RF(:,1) )¦C(:,6)¦RF(:,4)) | C(:,1).* (1 -(1 -C(:,3)).*(1 -RF(:,3))).* (1 -(1 -( 1 - (1 -C(:,7)).*(1 -C(:,8)).*(1 -C(:,9)).*(1 -C(:,10)).*(1 -C(:,11)).*(1 -C(:,12)).*(1 -RF(:,1)) )).*(1 -C(:,6)).*(1 -RF(:,4)))
TRC | Transient with loss of Reactor Control | C(:,4) & (RF(:,3)¦C(:,3)) | C(:,4).* (1 -(1 -RF(:,3)).*(1 -C(:,3)))
TEW | Failure of the long-term heat removal system | C(:,1) & ~( C(:,7) ¦ C(:,8) ¦ C(:,9) ¦ C(:,10) ¦ C(:,11) ¦ C(:,12) ¦ RF(:,1) ) & ((~C(:,13) & RF(:,2)) ¦ (~C(:,2) & C(:,13))) | C(:,1).* (1 -( 1 - (1 -C(:,7)).*(1 -C(:,8)).*(1 -C(:,9)).*(1 -C(:,10)).*(1 -C(:,11)).*(1 -C(:,12)).*(1 -RF(:,1)) )) .*(1 -(1 -(1 -C(:,13)).*RF(:,2)).*(1 -(1 -C(:,2)).*C(:,13)))
CM | Core Meltdown | C(:,4) ¦ C(:,5) ¦ C(:,1) & (( C(:,7) ¦ C(:,8) ¦ C(:,9) ¦ C(:,10) ¦ C(:,11) ¦ C(:,12) ¦ RF(:,1) ) ¦ (C(:,3)¦RF(:,3))&(C(:,6)¦RF(:,4)) ¦ (C(:,13)¦RF(:,2))) | 1 -(1 -C(:,4)).*(1 -C(:,5)).*(1 -C(:,1).*( 1 -(1 -( 1 - (1 -C(:,7)).*(1 -C(:,8)).*(1 -C(:,9)).*(1 -C(:,10)).*(1 -C(:,11)).*(1 -C(:,12)).*(1 -RF(:,1)) )).*(1 -( (1 -(1 -C(:,3)).*(1 -RF(:,3))).*(1 -(1 -C(:,6)).*(1 -RF(:,4))) )).*(1 -( 1 -(1 -C(:,13)).*(1 -RF(:,2)) )) ))
(1) Example Fault Tree for CM & (2) Mathematical Expressions:
(1)
(2)

## Solver Setting
Terminologies: UMB(Uni-Modal Bound), DQFM(Direct Quantification of the Fault Tree using Monte Carlo Simulation), IDQFM(Improved DQFM)
Risk Quantification Methods | Seismic Intensity Discretizations (PGA, unit: g) |  |  | Number of samples for each seismic intesity (Only for sampling-based method)
| Initial | Last | Subdivision
Boolean Algebra (UMB) | 0.05 | 2 | 0.1 | -
Original DQFM (DQFM) | 0.05 | 2 | 0.1 | 10000
Improved DQFM (IDQFM) | 0.05 | 2 | 0.1 | 10000

## Expected Output
Expected Output Examples:
(1) Hazard Curve Input and Confirmation
(2) Component Seismic Fragility Curve Input and Confirmation
(3) System Fragility Results
(4) System Risk Result Bar
(5) System Risk Result Tables
(1)
(2)
(3)
(4)
(5)